## How to use
Proxy Asset Replacement Cost tool
Version: 0.3
Colour coding
Cells coloured light yellow: Assumptions. Can edit if experienced, otherwise leave as is and enter Actual values in green cells
Cells not filled: formulas and information the user should not edit
Cells where input can be provided
Contents
Generic Diagram |  | Simplified network diagram outlining HV/MV/LV split principles
1. Inputs |  | Main user inputs
2. Asset qty Calc |  | Refined user inputs and fine tuning
3. Asset Cost Calc |  | Calculation of asset replacement cost and HV?MV?LV split
4. Escalation |  | Used for escalation parameter inputs
Detailed costing sheet Substations |  | Detailed bills of quantities sheet for substations and "per bay" calculations
Detailed costing sheet Retic |  | Detailed bills of quantities sheet for underground reticulation "per unit" calculations
Detailed costing sheet OHL |  | Detailed bills of quantities sheet for underground OHL "per unit" calculations

## Generic Diagram
≥44 kV
6.6; 11; 22; 33 kV
400V
400V
U/g feeder
O/h feeder
HV
MV
LV
HV bulk customer
MV bulk customers
LV bulk customer (urban)
LV bulk customer (urban / rural)
LV domestic / small commercial customers (urban / rural)
LV domestic / small commercial customers (urban)
Transformer
RMU
LV Metering / distribution kiosk
LV Pole top box
Customer / customer group
Substation bus
MV Pole
MV Feeder (Line or cable)
LV Feeder (Line or cable)

## 1. Inputs
XYZ LOCAL MUNICIPALITY
ASSET VALUE ESTIMATION METHOD
INPUT SHEET
1 | Municipality | XYZ LOCAL MUNICIPALITY
2 | Supply points
| Supply point | 1 | 2 | 3 | 4 | 5 | TOTAL
Connection voltage (kV)
| NMD (kVA) | [5 empty] | 0
| Energy Purchased (kWh) | [5 empty] | 0
| Demand purchased (kVA) | [5 empty] | 0
3 | Main network elements |  | Per supply point
| Main network elements | Qty - Supply point 1 | Qty - Supply point 2 | Qty - Supply point 3 | Qty - Supply point 4 | Qty - Supply point 5
Secondary MV voltage: 22 , 6.6 or 11 - (kV)
33kV present? (Yes/No)
No. of Primary substations, i.e. HV/MV (if known)
No. of HV Cable Feeders
No. of HV Line Feeders
HV Cable Feeder lenth (km route)
HV Line Feeder length (km route)
No. of HV/MV Transformers - installed at Main supply points
No. of HV/MV transformers - installed at other substations
HV/MV Transformer installed capacity (kVA) at main intake points
HV/MV Transformer installed capacity (kVA) at other substations
No. of 33kV/MV substations
No. of MV cable feeders (33kV)
No. of MV cable feeders (11kV or 6.6kV)
No. of MV overhead line feeders
No. of MV/LV Minisubs
No. of MV/LV building mounted transformers
No. of MV/LV pole mounted transformers
MV/LV Transformer installed capacity (kVA)
No. of HV customers
No. of MV customers
No. of LV bulk customers
No. of LV small commercial consumers
No. of LV Domestic consumers
4 | % Guestimate of network to customers
| Supply point | 1 | 2 | 3 | 4 | 5
Underground
Overhead
Below section is not used
5 | NERSA Form D Energy Sales |  |  |  |  | Additional parameters against tariff
| Tariff Name | Load profile code | Tariff structure code | Number of consumers | Energy Sales (kWh) | Network level (HV/MV/LV) | kVA / consumer / month (demand charge) | kVA / consumer / month (network access charge) | kVarh / consumer / month | Load factor
Note on C51: Load Profile Code Categories Description LP Code 1: Residential low usage, Electrification Low consumption, high peaks LP Code 2: Residential, Developing Township Morning/Evening peak LP Code 3: Residential. Established Township Morning/Evening peak LP Code 4: Commercial Morning peak, low night load LP Code 5: Light Industry Daytime essentially constant LP Code 6: Heavy Industry Essentially constant LP Code 7: Mining Essentially constant LP Code 8: Agriculture Long feeders, variable load LP Code 9: Traction/Transportation Medium to high load factor LP Code 10: Rural, not included in Category 1 above Long feeders, low load factor LP Code 11: Other
Note on D51: Tariff Structure Code Categories (Per Interim National Distribution Tariff System December 1995 - chapter 5) TS Code 5.1: One part single energy rate TS Code 5.2: Two Part TS Code 5.3: Two Part Time of Use TS Code 5.4: Three Part TS Code 5.5: Three Part Time of Use TS Code 5.6: Other / Special
Note on C52: Load Profile Code Categories Description LP Code 1: Residential low usage, Electrification Low consumption, high peaks LP Code 2: Residential, Developing Township Morning/Evening peak LP Code 3: Residential. Established Township Morning/Evening peak LP Code 4: Commercial Morning peak, low night load LP Code 5: Light Industry Daytime essentially constant LP Code 6: Heavy Industry Essentially constant LP Code 7: Mining Essentially constant LP Code 8: Agriculture Long feeders, variable load LP Code 9: Traction/Transportation Medium to high load factor LP Code 10: Rural, not included in Category 1 above Long feeders, low load factor LP Code 11: Other
Note on D52: Tariff Structure Code Categories (Per Interim National Distribution Tariff System December 1995 - chapter 5) TS Code 5.1: One part single energy rate TS Code 5.2: Two Part TS Code 5.3: Two Part Time of Use TS Code 5.4: Three Part TS Code 5.5: Three Part Time of Use TS Code 5.6: Other / Special
Note on C53: Load Profile Code Categories Description LP Code 1: Residential low usage, Electrification Low consumption, high peaks LP Code 2: Residential, Developing Township Morning/Evening peak LP Code 3: Residential. Established Township Morning/Evening peak LP Code 4: Commercial Morning peak, low night load LP Code 5: Light Industry Daytime essentially constant LP Code 6: Heavy Industry Essentially constant LP Code 7: Mining Essentially constant LP Code 8: Agriculture Long feeders, variable load LP Code 9: Traction/Transportation Medium to high load factor LP Code 10: Rural, not included in Category 1 above Long feeders, low load factor LP Code 11: Other
Note on D53: Tariff Structure Code Categories (Per Interim National Distribution Tariff System December 1995 - chapter 5) TS Code 5.1: One part single energy rate TS Code 5.2: Two Part TS Code 5.3: Two Part Time of Use TS Code 5.4: Three Part TS Code 5.5: Three Part Time of Use TS Code 5.6: Other / Special
Note on C54: Load Profile Code Categories Description LP Code 1: Residential low usage, Electrification Low consumption, high peaks LP Code 2: Residential, Developing Township Morning/Evening peak LP Code 3: Residential. Established Township Morning/Evening peak LP Code 4: Commercial Morning peak, low night load LP Code 5: Light Industry Daytime essentially constant LP Code 6: Heavy Industry Essentially constant LP Code 7: Mining Essentially constant LP Code 8: Agriculture Long feeders, variable load LP Code 9: Traction/Transportation Medium to high load factor LP Code 10: Rural, not included in Category 1 above Long feeders, low load factor LP Code 11: Other
Note on D54: Tariff Structure Code Categories (Per Interim National Distribution Tariff System December 1995 - chapter 5) TS Code 5.1: One part single energy rate TS Code 5.2: Two Part TS Code 5.3: Two Part Time of Use TS Code 5.4: Three Part TS Code 5.5: Three Part Time of Use TS Code 5.6: Other / Special
Note on C55: Load Profile Code Categories Description LP Code 1: Residential low usage, Electrification Low consumption, high peaks LP Code 2: Residential, Developing Township Morning/Evening peak LP Code 3: Residential. Established Township Morning/Evening peak LP Code 4: Commercial Morning peak, low night load LP Code 5: Light Industry Daytime essentially constant LP Code 6: Heavy Industry Essentially constant LP Code 7: Mining Essentially constant LP Code 8: Agriculture Long feeders, variable load LP Code 9: Traction/Transportation Medium to high load factor LP Code 10: Rural, not included in Category 1 above Long feeders, low load factor LP Code 11: Other
Note on D55: Tariff Structure Code Categories (Per Interim National Distribution Tariff System December 1995 - chapter 5) TS Code 5.1: One part single energy rate TS Code 5.2: Two Part TS Code 5.3: Two Part Time of Use TS Code 5.4: Three Part TS Code 5.5: Three Part Time of Use TS Code 5.6: Other / Special
Note on C56: Load Profile Code Categories Description LP Code 1: Residential low usage, Electrification Low consumption, high peaks LP Code 2: Residential, Developing Township Morning/Evening peak LP Code 3: Residential. Established Township Morning/Evening peak LP Code 4: Commercial Morning peak, low night load LP Code 5: Light Industry Daytime essentially constant LP Code 6: Heavy Industry Essentially constant LP Code 7: Mining Essentially constant LP Code 8: Agriculture Long feeders, variable load LP Code 9: Traction/Transportation Medium to high load factor LP Code 10: Rural, not included in Category 1 above Long feeders, low load factor LP Code 11: Other
Note on D56: Tariff Structure Code Categories (Per Interim National Distribution Tariff System December 1995 - chapter 5) TS Code 5.1: One part single energy rate TS Code 5.2: Two Part TS Code 5.3: Two Part Time of Use TS Code 5.4: Three Part TS Code 5.5: Three Part Time of Use TS Code 5.6: Other / Special
Note on C57: Load Profile Code Categories Description LP Code 1: Residential low usage, Electrification Low consumption, high peaks LP Code 2: Residential, Developing Township Morning/Evening peak LP Code 3: Residential. Established Township Morning/Evening peak LP Code 4: Commercial Morning peak, low night load LP Code 5: Light Industry Daytime essentially constant LP Code 6: Heavy Industry Essentially constant LP Code 7: Mining Essentially constant LP Code 8: Agriculture Long feeders, variable load LP Code 9: Traction/Transportation Medium to high load factor LP Code 10: Rural, not included in Category 1 above Long feeders, low load factor LP Code 11: Other
Note on D57: Tariff Structure Code Categories (Per Interim National Distribution Tariff System December 1995 - chapter 5) TS Code 5.1: One part single energy rate TS Code 5.2: Two Part TS Code 5.3: Two Part Time of Use TS Code 5.4: Three Part TS Code 5.5: Three Part Time of Use TS Code 5.6: Other / Special
Note on C58: Load Profile Code Categories Description LP Code 1: Residential low usage, Electrification Low consumption, high peaks LP Code 2: Residential, Developing Township Morning/Evening peak LP Code 3: Residential. Established Township Morning/Evening peak LP Code 4: Commercial Morning peak, low night load LP Code 5: Light Industry Daytime essentially constant LP Code 6: Heavy Industry Essentially constant LP Code 7: Mining Essentially constant LP Code 8: Agriculture Long feeders, variable load LP Code 9: Traction/Transportation Medium to high load factor LP Code 10: Rural, not included in Category 1 above Long feeders, low load factor LP Code 11: Other
Note on D58: Tariff Structure Code Categories (Per Interim National Distribution Tariff System December 1995 - chapter 5) TS Code 5.1: One part single energy rate TS Code 5.2: Two Part TS Code 5.3: Two Part Time of Use TS Code 5.4: Three Part TS Code 5.5: Three Part Time of Use TS Code 5.6: Other / Special
Note on C59: Load Profile Code Categories Description LP Code 1: Residential low usage, Electrification Low consumption, high peaks LP Code 2: Residential, Developing Township Morning/Evening peak LP Code 3: Residential. Established Township Morning/Evening peak LP Code 4: Commercial Morning peak, low night load LP Code 5: Light Industry Daytime essentially constant LP Code 6: Heavy Industry Essentially constant LP Code 7: Mining Essentially constant LP Code 8: Agriculture Long feeders, variable load LP Code 9: Traction/Transportation Medium to high load factor LP Code 10: Rural, not included in Category 1 above Long feeders, low load factor LP Code 11: Other
Note on D59: Tariff Structure Code Categories (Per Interim National Distribution Tariff System December 1995 - chapter 5) TS Code 5.1: One part single energy rate TS Code 5.2: Two Part TS Code 5.3: Two Part Time of Use TS Code 5.4: Three Part TS Code 5.5: Three Part Time of Use TS Code 5.6: Other / Special
Note on C60: Load Profile Code Categories Description LP Code 1: Residential low usage, Electrification Low consumption, high peaks LP Code 2: Residential, Developing Township Morning/Evening peak LP Code 3: Residential. Established Township Morning/Evening peak LP Code 4: Commercial Morning peak, low night load LP Code 5: Light Industry Daytime essentially constant LP Code 6: Heavy Industry Essentially constant LP Code 7: Mining Essentially constant LP Code 8: Agriculture Long feeders, variable load LP Code 9: Traction/Transportation Medium to high load factor LP Code 10: Rural, not included in Category 1 above Long feeders, low load factor LP Code 11: Other
Note on D60: Tariff Structure Code Categories (Per Interim National Distribution Tariff System December 1995 - chapter 5) TS Code 5.1: One part single energy rate TS Code 5.2: Two Part TS Code 5.3: Two Part Time of Use TS Code 5.4: Three Part TS Code 5.5: Three Part Time of Use TS Code 5.6: Other / Special
Note on C61: Load Profile Code Categories Description LP Code 1: Residential low usage, Electrification Low consumption, high peaks LP Code 2: Residential, Developing Township Morning/Evening peak LP Code 3: Residential. Established Township Morning/Evening peak LP Code 4: Commercial Morning peak, low night load LP Code 5: Light Industry Daytime essentially constant LP Code 6: Heavy Industry Essentially constant LP Code 7: Mining Essentially constant LP Code 8: Agriculture Long feeders, variable load LP Code 9: Traction/Transportation Medium to high load factor LP Code 10: Rural, not included in Category 1 above Long feeders, low load factor LP Code 11: Other
Note on D61: Tariff Structure Code Categories (Per Interim National Distribution Tariff System December 1995 - chapter 5) TS Code 5.1: One part single energy rate TS Code 5.2: Two Part TS Code 5.3: Two Part Time of Use TS Code 5.4: Three Part TS Code 5.5: Three Part Time of Use TS Code 5.6: Other / Special
Note on C62: Load Profile Code Categories Description LP Code 1: Residential low usage, Electrification Low consumption, high peaks LP Code 2: Residential, Developing Township Morning/Evening peak LP Code 3: Residential. Established Township Morning/Evening peak LP Code 4: Commercial Morning peak, low night load LP Code 5: Light Industry Daytime essentially constant LP Code 6: Heavy Industry Essentially constant LP Code 7: Mining Essentially constant LP Code 8: Agriculture Long feeders, variable load LP Code 9: Traction/Transportation Medium to high load factor LP Code 10: Rural, not included in Category 1 above Long feeders, low load factor LP Code 11: Other
Note on D62: Tariff Structure Code Categories (Per Interim National Distribution Tariff System December 1995 - chapter 5) TS Code 5.1: One part single energy rate TS Code 5.2: Two Part TS Code 5.3: Two Part Time of Use TS Code 5.4: Three Part TS Code 5.5: Three Part Time of Use TS Code 5.6: Other / Special

## 2. Asset Qty Calc
XYZ LOCAL MUNICIPALITY
ASSET VALUE ESTIMATION METHOD
HIGH LEVEL ASSET QUANTITY CALCULATION
CALCULATION BASED ON NOTIFIED MAXIMUM DEMAND
| Parameter | Notes | All supply points combined | Supply point 1 |  |  |  | Supply point 2 |  |  |  | supply point 3 |  |  |  | supply point 4 |  |  |  | supply point 5
|  |  | Total Utilized Values | Assumed value | Calculated value | Actual value | Utilized value | Assumed value | Calculated value | Actual value | Utilized value | Assumed value | Calculated value | Actual value | Utilized value | Assumed value | Calculated value | Actual value | Utilized value | Assumed value | Calculated value | Actual value | Utilized value
1 | Total demand (kVA) |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
2 | NMD (kVA) |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
3 | Main substations
| Total no. of Main substations |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
| Primary Substation Transformer Size |  | 0 | 20000 | 0 | 20000 | 0 | 20000 | 0 |  | 0 | 20000 | 0 |  | 0 | 20000 | 0 |  | 0 | 20000 | 0 |  | 0
| Primary substation Firm Capacity |  | 0 | 40000 |  |  | 0 | 40000 |  |  | 0 | 40000 |  |  | 0 | 40000 |  |  | 0 | 40000 |  |  | 0
| Total number of HV/MV transformers (not 33kV) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Total number of HV/33kV transformers |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
4 | Main intermediate MV/MV substations (e.g. 33/11kV)
| Total No. of MV/MV substations (e.g. 33/11kV) |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
| MV/MV (e.g. 33/11kV) Substation transformer size (kVA) |  | 0 | 10000 |  |  | 0 | 10000 |  |  | 0 | 10000 |  |  | 0 | 10000 |  |  | 0 | 10000 |  |  | 0
| MV/MV (e.g. 33/11kV) Substation firm capacity |  | 0 | 10000 |  |  | 0 | 10000 |  |  | 0 | 10000 |  |  | 0 | 10000 |  |  | 0 | 10000 |  |  | 0
| Total number of MV/MV transformers |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Average 33kV main feeder cable length between substations (km) |  | 0 | 5 |  |  | 0 | 5 |  |  | 0 | 5 |  |  | 0 | 5 |  |  | 0 | 5 |  |  | 0
| Total 33kV feeder length |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| MV 33kV Underground (km) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0
| MV 33kV Overhead (km) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0
| Total 33kV feeders |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
5 | Switching substations
| Switching substation firm capacity (kVA) |  | 0 | 20000 |  |  | 0 | 20000 |  |  | 0 | 20000 |  |  | 0 | 20000 |  |  | 0 | 20000 |  |  | 0
| Total no. of switching substations |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Switching substation main incomer capacity | 240PILC(Cu) | 0 | 7000 |  |  | 0 | 7000 |  |  | 0 | 7000 |  |  | 0 | 7000 |  |  | 0 | 7000 |  |  | 0
| No. of switching substation incomers per substation |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Average distance of MV cable between main substations and switching substations (km) |  | 0 | 2.5 |  |  | 0 | 2.5 |  |  | 0 | 2.5 |  |  | 0 | 2.5 |  |  | 0 | 2.5 |  |  | 0
| Total Primary MV cable length (Main substations to switching substations) - km |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
6 | MV Feeders
| Typical MV feeder capacity (kVA) | 6MVA when using 185PILC(Cu) or 120XLPE(Cu) | 0 | 6000 |  |  | 0 | 6000 |  |  | 0 | 6000 |  |  | 0 | 6000 |  |  | 0 | 6000 |  |  | 0
| Total no. of MV feeders |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
| No. of MV feeders per switching station |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| MV/LV transformer average size (kVA) | 400-600kVA, unless mostly from overhead network (100-200kVA) | 0 | 500 |  |  | 0 | 500 |  |  | 0 | 500 |  |  | 0 | 500 |  |  | 0 | 500 |  |  | 0
| No. of MV/LV transformers |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
| Minisubs |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Pole mounted transformers |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| No. MV/LV transformers per ring |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Average distance of MV cable between MV/LV transformers (m) | 300 to 400m | 0 | 300 |  |  | 0 | 300 |  |  | 0 | 300 |  |  | 0 | 300 |  |  | 0 | 300 |  |  | 0
| Total length MV cable (km) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| MV Underground (km) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0
| MV Overhead (km) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0
| Total length MV per ring (km) | 4-6km | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
7 | LV Feeders
| No. of LV feeders per MV/LV transformer |  | 0 | 5 |  |  | 0 | 5 |  |  | 0 | 5 |  |  | 0 | 5 |  |  | 0 | 5 |  |  | 0
| Total No. of LV feeders |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Average length of LV feeder (m) | 200-400m | 0 | 250 |  |  | 0 | 250 |  |  | 0 | 250 |  |  | 0 | 250 |  |  | 0 | 250 |  |  | 0
| Total LV feeder length (km) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| LV Underground (km) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| LV Overhead (km) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| No. of connections per kiosk |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
| Spacing between kiosks |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0
| No. of distribution / metering kiosks |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Number of LV connections (non-bulk) |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
8 | Public lighting
| Average spacing between streetlights (m) |  | 0 | 40 |  |  | 0 | 40 |  |  | 0 | 40 |  |  | 0 | 40 |  |  | 0 | 40 |  |  | 0
| Average stand size (m2) |  | 0 | 600 |  |  | 0 | 600 |  |  | 0 | 600 |  |  | 0 | 600 |  |  | 0 | 600 |  |  | 0
| Total streetlength (km) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Total Streetlights |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Total streetlight cable (km) |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Highmast lights |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Note: This calculation is not distinguishing between overhead and underground infrastructure. The distinguishing of it is done on the next sheet utilizing the estimated % split between overhead and underground infrastructure

## 3. Asset Cost Calc
XYZ LOCAL MUNICIPALITY
ASSET VALUE ESTIMATION METHOD
PROXY ASSET REGISTER - REPLACEMENT VALUE ESTIMATION ONLY
A | B | C | E | F
Major summarized item (for detailed cost calculation, refer to detailed costing sheet for substation works or MV/LV reticulation works | UoM | Total Qty | Cost per unit | Total cost
HV Incomer bays - Outdoor | ea | 0 | 4820000 | 0
HV outdoor Busbar,bussectionalizers & related shared infrastructure | Lot | 0 | 18720000 | 0
HV Outdoor Feeder breakers | ea | 0 | 6030000 | 0
HV cable feeder length | km | 0 | 11543344.3427 | 0
HV line feeder length | km | 0 | 3900000 | 0
HV/33kV transformers | ea | 0 | 18720000 | 0
HV/11kV transformers | ea | 0 | 18720000 | 0
33 kV incomer bays (Main sub) | ea | 0 | 2370000 | 0
33 kV busbar (Main sub) (incl. all building works & common services) | Lot | 0 | 12530000 | 0
33 kV outdoor feeders (Main sub) | ea | 0 | 2210000 | 0
33kV cables | km | 0 | 6300000 | 0
33KV OHL | km | 0 | 757277.4772 | 0
33/11kV transformers | ea | 0 | 12750000 | 0
11kV incomers - main sub | ea | 0 | 1200000 | 0
11kV busbars - main sub (incl. all building works & common services) | Lot | 0 | 8930000 | 0
11kV Feeders - main sub | ea | 0 | 1070000 | 0
11kV primary feeder ring | km | 0 | 1500000 | 0
11kV incomers - switching sub | ea | 0 | 804000 | 0
11kV busbars - switching sub (incl. all building works & common services) | Lot | 0 | 4623000 | 0
11kV Feeders - switching sub | ea | 0 | 704000 | 0
11kV secondary feeder ring | km | 0 | 980000 | 0
Ring main unit with CT/VT unit | ea | 0 | 555000 | 0
11kV/400V minisub | ea | 0 | 761000 | 0
4-core LV feeder | km | 0 | 850000 | 0
LV Kiosk | ea | 0 | 18300 | 0
11kV Overhead line | km | 0 | 582521.1363 | 0
Pole transformer | ea | 0 | 170013.1898 | 0
LV overhead line | km | 0 | 1001422.9396 | 0
Total estimated Replacement Asset Value |  |  |  | 0
This method uses an estimation process of asset quantities |  |  | Summary of network level; contribution to asset value
based on typical replacement values |  |  | Network level | Estimated asset value | % Network level
Network quantities have been estimated from the NMD |  |  | HV | 0 | #DIV/0!
and from user input values |  |  | MV | 0 | #DIV/0!
|  |  | LV | 0 | #DIV/0!
|  |  | Check total | 0 | #DIV/0!
INPUT ASSUMPTIONS — referenced by the 'Cost per unit' column above
HV cable feeder — base rate per km, in Dec 2016 money |  |  | 5000000 | Escalated to Jun-26 via WG 162. Base index Dec 2016 = 100.
33kV OHL — uplift factor over the 11kV OHL rate |  |  | 1.3 | Applied to 'Detail costing OHL'!H201 (already escalated).
Note on C6: Zibusiso Ndlovu: Unit of Measurement
Note on E47: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: HV cable feeder base rate, R5 000 000 per km, expressed in Dec 2016 money. Originally embedded in E10 as =5000*1000*(1.08^5) - a flat 8% per year for 5 years, which bypassed the P0151 index. Replaced with the actual WG 162 index ratio. Provenance inferred: the 1.08^5 carried a Dec-2016 rate forward to 2021, matching the sheet's original Aug-2021 current index. Cross-check: WG 162 at Aug-2021 was 163,4, giving R8,17m against the old formula's R7,35m - same order, the flat 8% just ran cooler than the actual index.
Note on E48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Uplift applied to the 11kV overhead line rate to proxy a 33kV line. Previously hardcoded as *1.3 inside E18 with no label or source. Value unchanged - only made visible.

## 4.Escalation
Stats SA P0151 publication
Base index:
| Electrical Installations | Electrical Reticulation |  | Year-on-Year increase |  | Stats SA P0151 Base date Dec 2016 = 100
| WG 160 | WG 162 |  | Electrical Installations | Electrical Reticulation
2017-06-01 | 98.7 | 99.7 |  | WG 160 | WG 162
2018-06-01 | 109.6 | 111.9 |  | 11.04% | 12.24%
2019-06-01 | 111.5 | 111.2 |  | 1.734% | -0.6256%
2020-06-01 | 117.3 | 118.4 |  | 5.202% | 6.475%
2021-06-01 | 161.2 | 164.5 |  | 37.43% | 38.94%
2021-08-01 | 159.8 | 163.4 |  |  |  | If no index is indicated in the rates, then this base index applies
| Use for labour | Use for material
Adjustable indices
| Electrical Installations | Electrical Reticulation | Running account of latest indices
| WG 160 | WG 162 | Date used | WG160 used | WG162 used
2021-01-01 | 134.8 | 136.7 | 2021-01-01 | 134.8 | 136.7 | The user can enter new dates and new indices as required in the first three columns.
2021-02-01 | 139.6 | 142.2 | 2021-02-01 | 139.6 | 142.2
2021-03-01 | 142.3 | 145.4 | 2021-03-01 | 142.3 | 145.4
2021-04-01 | 148.4 | 153 | 2021-04-01 | 148.4 | 153
2021-05-01 | 153.7 | 156.6 | 2021-05-01 | 153.7 | 156.6
2021-06-01 | 161.2 | 164.5 | 2021-06-01 | 161.2 | 164.5
2021-07-01 | 157.7 | 160.1 | 2021-07-01 | 157.7 | 160.1
2021-08-01 | 159.8 | 163.4 | 2021-08-01 | 159.8 | 163.4
2026-06-01 | 210.1567 | 230.8669 | 2026-06-01 | 210.1567 | 230.8669
|  |  | 2026-06-01 | 210.1567 | 230.8669
|  |  | 2026-06-01 | 210.1567 | 230.8669
|  |  | 2026-06-01 | 210.1567 | 230.8669
Latest index used |  |  | 2026-06-01 | 210.1567 | 230.8669 | These values are used in calculations to adjust the base rates against a base index.
New rate = Rate x Latest index / Base index
RE-BASING BLOCK — converts Dec 2023 = 100 indices onto this sheet's Dec 2016 = 100 base
The series has been re-based TWICE since this sheet was built: Dec 2016 = 100 -> Dec 2021 = 100 -> Dec 2023 = 100. No single release spans 2021 to 2026, so we chain two links.
|  |  | WG 160 | WG 162
|  |  | Labour | Material
STEP 1 bridge Dec 2016 = 100 to Dec 2021 = 100 (via a month published on BOTH bases)
Overlap month used — Jun-21 chosen to match the sheet's June convention >>> |  |  | 2021-06-01
Its index on OLD Dec 2016 = 100 base <-- read from rows 16-23 of this sheet |  |  | 161.2 | 164.5
Its index on Dec 2021 = 100 base <-- read from the reference table at row 61 |  |  | 93.6 | 92.8
FACTOR 1 |  |  | 1.7222 | 1.7726
STEP 2 bridge Dec 2021 = 100 to Dec 2023 = 100
Dec 2023 index on Dec 2021 = 100 base (source: P0151 December 2023 release) |  |  | 103.5 | 105.8
Dec 2023 index on Dec 2023 = 100 base = 100 by definition |  |  | 100 | 100
FACTOR 2 |  |  | 1.035 | 1.058
COMBINED FACTOR = Factor 1 x Factor 2 |  |  | 1.7825 | 1.8754
JUNE 2026 index on NEW Dec 2023 = 100 base (from your P0151 June 2026 download) |  |  | 117.9 | 123.1
JUNE 2026 re-based to Dec 2016 = 100 --> flows into row 24 automatically |  |  | 210.1567 | 230.8669
HOW TO UPDATE THIS SHEET NEXT YEAR
1. Download the Stats SA P0151 release for JUNE of the year you are valuing. Table 1 carries the CPAP work group indices.
2. Overwrite E49 with WG 160 (Electrical installations = LABOUR) and F49 with WG 162 (Electrical reticulation = MATERIAL) for that June.
3. Check the base printed above Table 1. If it still reads 'Base: Dec 2023=100', you are finished - row 24, row 28 and every rate in the workbook update themselves.
4. If Stats SA has re-based again, add a further link below Step 2 using the same pattern: a re-base month equals 100 on its own base, so the factor is simply (index on the previous base) / 100.
Sources: Factor 1 from the P0151 February 2022 release. Factor 2 from the P0151 December 2023 release. June 2026 figures from the P0151 June 2026 release. Each cell carries a full citation on hover.
Rows 16 to 23 (red outline) stay on the OLD Dec 2016 base and must never be edited - 268 rate formulas look them up as base indices.
REFERENCE — 2021 indices on the Dec 2021 = 100 base
Source: Stats SA, Construction Materials Price Indices, February 2022 (P0151.1), Table 1 — CPAP work group indices, Base: Dec 2021=100
Month | WG 160 | WG 162
2021-02-01 | 81 | 80.2
2021-03-01 | 82.6 | 82
2021-04-01 | 86.1 | 86.3
2021-05-01 | 89.2 | 88.3
2021-06-01 | 93.6 | 92.8
2021-07-01 | 92.3 | 90.7
2021-08-01 | 93.6 | 92.6
Formulas:
Running account of latest indices = IF([Electrical Installations]<>"", B17, [Running account of latest indices, row above])
Running account of latest indices = [Running account of latest indices, row above]
Note on B16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: DO NOT CHANGE rows 16 to 23. These Jan-Aug 2021 indices are on the OLD Dec 2016 = 100 base and are the BASE indices that 268 rate formulas on the two detailed costing sheets look up by base date (Jan-2021). Overwriting them causes #N/A across the workbook.
Note on C24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Do not type here. Formula pulling the re-based June 2026 value from E50.
Note on E38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Overlap month. Jun-21 chosen because the guideline uses the June value. May be changed to any month Feb-21 to Aug-21; both lookups follow. Note: Jul-21 and Aug-21 give a factor about 0,8% lower, because the Dec 2016 base figures in rows 16-23 were revised by Stats SA after this sheet captured them. Feb-Jun are mutually consistent.
Note on E43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: Stats SA, Construction Material Price Indices, December 2023 (P0151.1), Table 1 - CPAP work group indices, Base: Dec 2021=100. Work group 160 - Electrical installations, Dec 2023 = 103,5.
Note on F43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: Stats SA, Construction Material Price Indices, December 2023 (P0151.1), Table 1 - CPAP work group indices, Base: Dec 2021=100. Work group 162 - Electrical reticulation, Dec 2023 = 105,8.
Note on E49: Zibusiso Ndlovu: Source: Stats SA, Construction Material Price Indices, June 2026 (P0151.1), Table 1 - CPAP work group indices, Base: Dec 2023=100. Work group 160 - Electrical installations, Jun 2026 = 117,9.
Note on F49: Zibusiso Ndlovu: Source: Stats SA, Construction Material Price Indices, June 2026 (P0151.1), Table 1 - CPAP work group indices, Base: Dec 2023=100. Work group 162 - Electrical reticulation, Jun 2026 = 123,1.

## Detail costing substation works
XYZ LOCAL MUNICIPALITY
ASSET VALUE ESTIMATION METHOD
CALCULATION SHEET FOR SUBSTATION UNIT COSTS
A | B | C | [5 empty] | D |  | E | F | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U
[8 empty] | No of Bays >>> |  |  |  | 1 | 2 | 1 | 2 | 2 | 2 | 1 | 2 | 14600 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 8
No. | Description | UoM | Material rate @ Base date | Labour rate @ Base date | Base date [YYYY/MM/01 -will display MMM-YY] | Escalation Material rate | Escalation Labour rate | Rate applied | Typical full substation QTY | Total Qty | Total amount | 88kV incoming line | 88kV Incomer bays - Outdoor | 88kV outdoor Busbar & bussectionalizers and other common associated cost | 88kV Outdoor Feeder breakers | 88/33kV transformer bay | 33kV Outdoor Incomers (Primary sub) | 33kV Outdoor bus-setionalizers, other common and associated cost (Primary sub) | 33kV outdoor feeders (Primary sub) | 2x 33kV 800mm2 Al 3x1C feeders XLPE | 33kV Indoor Incomers (33/11kV sub) | 33kV Indoor bus-setionalizers, other common and associated cost (33/11kV sub) | 33kV Indoor feeders (33/11kV sub) | 33/11kV transformer bay | 88/11kV transformer bay | 11kV incomers (Main sub) | 11kV bus-couplers and other common associated cost (Main sub) | 11kV feeder breakers (Main sub)
1 | Preliminary & General cost | Sum |  | 8% |  |  |  | 20531558.8262 | 1 | 1 | 20531558.8262 | 6.299% | 3.115% | 6.046% | 3.898% | 12.09% | 1.532% | 4.046% | 1.43% | 29.49% | 1.864% | 3.174% | 1.492% | 8.237% | 10.87% | 0.7773% | 2.883% | 2.758%
2 | Sub-station building, earthworks etc.
2.1 | Substation Earthworks, Platform, Access road, Stormwater drainage etc. | m2 | 640.29 | 463.63 | 2021-01-01 | 168.9% | 155.9% | 1804.17 | 8250 | E: 7500; F: 13531275; G: 2500; K: 2500; O: 1250; T: 1250
2.2 | Earthmat | m2 | 112.09 | 100.26 | 2021-01-01 | 168.9% | 155.9% | 345.61 | 8250 | E: 7500; F: 2592075; G: 2500; K: 2500; O: 1250; T: 1250
2.3 | 25-35mm dia Yardstone 100mm thick layer | m² | 78 | 12 | 2021-01-01 | 168.9% | 155.9% | 150.44 | 565.2 | E: 7500; F: 1128300; G: 2500; K: 2500; O: 1250; T: 1250
2.4 | Galvanised Pallissade Fence | m | 1213.83 | 476.21 | 2021-01-01 | 168.9% | 155.9% | 2792.41 | 660 | E: 400; F: 1116964; G: 125; K: 125; O: 75; T: 75
2.5 | Substation Building suitable for 33kV Indoor Switchgear & Control room | m² | 5520 | 2480 | 2021-01-01 | 168.9% | 155.9% | 13188.88 | 0 | E: 98; F: 1292510.24; O: 98
2.6 | Substation Building suitable for 11kV Indoor Switchgear. | m² | 5520 | 2480 | 2021-01-01 | 168.9% | 155.9% | 13188.88 | 400 | E: 72; F: 949599.36; T: 72
2.7 | Control Room | m² | 5520 | 2480 | 2021-01-01 | 168.9% | 155.9% | 13188.88 | 90 | E: 50; F: 659444; G: 25; K: 25
0
3 | Power Plant Work | [7 empty] | 0
3.1 | Excavations (support foundations) | [7 empty] | 0
3.1.1 | 33kV Kiosk Circuit breaker | ea |  | 1840 | 2021-08-01 | 141.3% | 131.5% | 2419.83 | 8 | E: 5; F: 12099.15; J: 2; K: 1; L: 2
3.1.2 | 88kV Circuitbreaker | ea |  | 2000 | 2021-08-01 | 141.3% | 131.5% | 2630.25 | 12 | E: 5; F: 13151.25; F: 2; G: 1; H: 2
3.1.3 | 33kV Isolator 2500A | ea |  | 1840 | 2021-08-01 | 141.3% | 131.5% | 2419.83 | 0 | E: 0; F: 0
3.1.4 | 88kV Isolator 2500A | ea |  | 2000 | 2021-08-01 | 141.3% | 131.5% | 2630.25 | 20 | E: 12; F: 31563; F: 4; G: 6; H: 2
3.1.5 | 88kV Tubular Busbar Support | ea |  | 860 | 2021-08-01 | 141.3% | 131.5% | 1131.01 | 11 | E: 4; F: 4524.04; F: 2; H: 2
3.1.6 | Medium Equipment Support | ea |  | 640 | 2021-08-01 | 141.3% | 131.5% | 841.68 | 49 | E: 19; F: 15991.92; F: 4; G: 6; H: 4; J: 2; K: 1; L: 2
3.1.7 | 88kV 132 C Column Foundation | ea |  | 2480 | 2021-08-01 | 141.3% | 131.5% | 3261.51 | 8 | E: 8; F: 26092.08; G: 8
3.1.8 | 14m Lighting Lightning Mast | ea |  | 2250 | 2021-08-01 | 141.3% | 131.5% | 2959.03 | 0 | E: 0; F: 0
3.1.9 | 21m Lighting Lightning Mast | ea |  | 2480 | 2021-08-01 | 141.3% | 131.5% | 3261.51 | 8 | E: 8; F: 26092.08; G: 2; K: 2; O: 2; T: 2
3.1.10 | 20-40MVA Transformer | ea |  | 14800 | 2021-08-01 | 141.3% | 131.5% | 19463.83 | 8 | E: 6; F: 116782.98; Q: 2; R: 2; T: 2
3.1.11 | MV Box Structure (Busbar) Column | ea |  | 1880 | 2021-08-01 | 141.3% | 131.5% | 2472.43 | 18 | E: 5; F: 12362.15; J: 2; K: 1; L: 2
3.1.12 | Cable End support | ea |  | 1000 | 2021-08-01 | 141.3% | 131.5% | 1315.12 | 4 | E: 0; F: 0
3.1.13 | NEC NER/AUX Transformer | ea |  | 880 | 2021-08-01 | 141.3% | 131.5% | 1157.31 | 4 | E: 6; F: 6943.86; I: 2; Q: 2; R: 2
3.1.14 | 33kV Knife Link Support | ea |  | 1840 | 2021-08-01 | 141.3% | 131.5% | 2419.83 | 0 | E: 0; F: 0
3.1.15 | Oil Holding dam | ea |  | 16000 | 2021-08-01 | 141.3% | 131.5% | 21041.98 | 1 | E: 3; F: 63125.94; I: 1; Q: 1; R: 1
0
3.2 | Concrete work Support Foundations - Including all | [7 empty] | 0
3.2.1 | 33kV Kiosk Circuit breaker | ea | 15000 | 4000 | 2021-08-01 | 141.3% | 131.5% | 26453.91 | 8 | E: 5; F: 132269.55; J: 2; K: 1; L: 2
3.2.2 | 88kV Circuitbreaker | ea | 20000 | 5000 | 2021-08-01 | 141.3% | 131.5% | 34833.5 | 12 | E: 5; F: 174167.5; F: 2; G: 1; H: 2
3.2.3 | 33kV Isolator 2500A | ea | 6000 | 2500 | 2021-08-01 | 141.3% | 131.5% | 11765.17 | 0 | E: 0; F: 0
3.2.4 | 88kV Isolator 2500A | ea | 9500 | 4500 | 2021-08-01 | 141.3% | 131.5% | 19340.55 | 20 | E: 12; F: 232086.6; F: 4; G: 6; H: 2
3.2.5 | 88kV Tubular Busbar Support | ea | 8000 | 3000 | 2021-08-01 | 141.3% | 131.5% | 15248.52 | 11 | E: 4; F: 60994.08; F: 2; H: 2
3.2.6 | Medium Equipment Support | ea | 6000 | 3500 | 2021-08-01 | 141.3% | 131.5% | 13080.3 | 49 | E: 19; F: 248525.7; F: 4; G: 6; H: 4; J: 2; K: 1; L: 2
3.2.7 | 88kV 132 C Column Foundation | ea | 28000 | 6000 | 2021-08-01 | 141.3% | 131.5% | 47451.77 | 8 | E: 8; F: 379614.16; G: 8
3.2.8 | 14m Lighting Lightning Mast | ea | 13000 | 4000 | 2021-08-01 | 141.3% | 131.5% | 23628.12 | 0 | E: 0; F: 0
3.2.9 | 21m Lighting Lightning Mast | ea | 28000 | 6000 | 2021-08-01 | 141.3% | 131.5% | 47451.77 | 8 | E: 8; F: 379614.16; G: 2; K: 2; O: 2; T: 2
3.2.10 | 20-40MVA Transformer | ea | 150000 | 35000 | 2021-08-01 | 141.3% | 131.5% | 257963.43 | 8 | E: 6; F: 1547780.58; Q: 2; R: 2; T: 2
3.2.11 | MV Box Structure Column | ea | 6000 | 2500 | 2021-08-01 | 141.3% | 131.5% | 11765.17 | 18 | E: 5; F: 58825.85; J: 2; K: 1; L: 2
3.2.12 | Cable End support | ea | 18000 | 5000 | 2021-08-01 | 141.3% | 131.5% | 32007.71 | 4 | E: 0; F: 0
3.2.13 | NEC NER/AUX Transformer | ea | 8000 | 3000 | 2021-08-01 | 141.3% | 131.5% | 15248.52 | 4 | E: 6; F: 91491.12; I: 2; Q: 2; R: 2
3.2.14 | 33kV Knife Link Support | ea | 6000 | 2500 | 2021-08-01 | 141.3% | 131.5% | 11765.17 | 0 | E: 0; F: 0
3.2.15 | Oil Holding dam | ea | 160000 | 40000 | 2021-08-01 | 141.3% | 131.5% | 278667.99 | 1 | E: 2; F: 557335.98; I: 1; Q: 0.5; R: 0.5
0
3.3 | Steelwork Equipment Supports | [7 empty] | 0
3.3.1 | 33kV Kiosk Circuit breaker | ea | 10000 | 1500 | 2021-08-01 | 141.3% | 131.5% | 16101.63 | 8 | E: 5; F: 80508.15; J: 2; K: 1; L: 2
3.3.2 | 88kV Circuitbreaker | ea | 18000 | 2500 | 2021-08-01 | 141.3% | 131.5% | 28719.9 | 12 | E: 3; F: 86159.7; F: 2; G: 1; H: 0
3.3.3 | 33kV Isolator 2500A | ea | 6000 | 1000 | 2021-08-01 | 141.3% | 131.5% | 9792.49 | 0 | E: 0; F: 0
3.3.4 | 88kV Isolator 2500A | ea | 7000 | 1200 | 2021-08-01 | 141.3% | 131.5% | 11468.41 | 20 | E: 12; F: 137620.92; F: 4; G: 6; H: 2
3.3.5 | 88kV Tubular Busbar Support | ea | 27000 | 3500 | 2021-08-01 | 141.3% | 131.5% | 42751.07 | 11 | E: 4; F: 171004.28; F: 2; H: 2
3.3.6 | Medium Equipment Support | ea | 5000 | 1000 | 2021-08-01 | 141.3% | 131.5% | 8379.59 | 49 | E: 19; F: 159212.21; F: 4; G: 6; H: 4; J: 2; K: 1; L: 2
3.3.7 | 88kV 132 C Column | ea | 45000 | 7000 | 2021-08-01 | 141.3% | 131.5% | 72786.1 | 8 | E: 8; F: 582288.8; G: 8
3.3.8 | 88kV 132 34 1 Beam | ea | 32000 | 5000 | 2021-08-01 | 141.3% | 131.5% | 51788.23 | 4 | E: 4; F: 207152.92; G: 4
3.3.9 | 14m Lighting Lightning Mast | ea | 38000 | 7000 | 2021-08-01 | 141.3% | 131.5% | 62895.84 | 0 | E: 0; F: 0
3.3.10 | 21m Lighting Lightning Mast | ea | 60000 | 12000 | 2021-08-01 | 141.3% | 131.5% | 100555.13 | 8 | E: 8; F: 804441.04; G: 2; K: 2; O: 2; T: 2
3.3.11 | MV Box Structure Complete per bay | ea | 6000 | 1000 | 2021-08-01 | 141.3% | 131.5% | 9792.49 | 18 | E: 5; F: 48962.45; J: 2; K: 1; L: 2
3.3.12 | Cable End support | ea | 22000 | 3500 | 2021-08-01 | 141.3% | 131.5% | 35686.6 | 4 | E: 0; F: 0
3.3.13 | NEC NER AUX Transformer | ea | 9000 | 2000 | 2021-08-01 | 141.3% | 131.5% | 15346.29 | 4 | E: 6; F: 92077.74; I: 2; Q: 2; R: 2
3.3.14 | 33kV Knife Link Support | ea | 22000 | 3500 | 2021-08-01 | 141.3% | 131.5% | 35686.6 | 0 | E: 0; F: 0
0
3.4 | Equipment | [7 empty] | 0
3.4.1 | 11kV Indoor Incomer Breaker | ea | 300000 | 10000 | 2021-01-01 | 168.9% | 155.9% | 522247.66 | 4 | E: 2; F: 1044495.32; S: 2
3.4.2 | 11kV Indoor Bus-Section Breaker | ea | 275000 | 10000 | 2021-01-01 | 168.9% | 155.9% | 480026.21 | 3 | E: 1; F: 480026.21; T: 1
3.4.3 | 11kV Indoor Feeder Breaker | ea | 250000 | 10000 | 2021-01-01 | 168.9% | 155.9% | 437804.76 | 10 | E: 8; F: 3502438.08; U: 8
3.4.4 | 33kV Kiosk Circuit breaker | ea | 600000 | 10000 | 2021-08-01 | 141.3% | 131.5% | 860887.66 | 8 | E: 9; F: 7747988.94; J: 2; K: 1; L: 2; Q: 4
3.4.5 | 88kV Circuitbreaker | ea | 520000 | 30000 | 2021-08-01 | 141.3% | 131.5% | 774158.61 | 12 | E: 5; F: 3870793.05; F: 2; G: 1; H: 2
3.4.6 | 88kV Isolator 2500A | ea | 200000 | 22000 | 2021-08-01 | 141.3% | 131.5% | 311511.53 | 20 | E: 12; F: 3738138.36; F: 4; G: 6; H: 2
3.4.7 | 88kV Current Transformer | ea | 155000 | 7500 | 2021-08-01 | 141.3% | 131.5% | 228862 | 39 | E: 18; F: 4119516; F: 6; G: 6; H: 6
3.4.8 | 88kV Voltage Transformer | ea | 110000 | 15000 | 2021-08-01 | 141.3% | 131.5% | 175145.2 | 6 | E: 6; F: 1050871.2; G: 6
3.4.9 | 33kV Indoor Incomer Breaker | ea | 1000000 | 10000 | 2021-08-01 | 141.3% | 131.5% | 1426045.28 | 0 | E: 2; F: 2852090.56; N: 2
3.4.10 | 33kV Indoor Bus-Section Breaker | ea | 650000 | 8000 | 2021-08-01 | 141.3% | 131.5% | 928902.12 | 0 | E: 1; F: 928902.12; O: 1
3.4.11 | 33kV Indoor Feeder Breaker | ea | 750000 | 8000 | 2021-08-01 | 141.3% | 131.5% | 1070191.52 | 0 | E: 4; F: 4280766.08; P: 2; R: 2
3.4.12 | 33kV Voltage Transformer | ea | 35000 | 2000 | 2021-08-01 | 141.3% | 131.5% | 52081.54 | 12 | E: 12; F: 624978.48; J: 6; N: 6
3.4.13 | 88/33kV 40MVA Transformer | ea | 10000000 | 120000 | 2021-08-01 | 141.3% | 131.5% | 14286755.27 | 4 | E: 2; F: 28573510.54; I: 2
3.4.14 | 88/11kV 20MVA Transformer | ea | 8000000 | 120000 | 2021-08-01 | 141.3% | 131.5% | 11460967.19 | 4 | E: 2; F: 22921934.38; R: 2
3.4.15 | 33/11kV 20MVA Transformer | ea | 5000000 | 120000 | 2021-08-01 | 141.3% | 131.5% | 7222285.05 | 4 | E: 2; F: 14444570.1; Q: 2
3.4.16 | NEC NER AUX Transformer 33kV | ea | 350000 | 20000 | 2021-08-01 | 141.3% | 131.5% | 520815.39 | 4 | E: 2; F: 1041630.78; I: 2
3.4.17 | NEC NER AUX Transformer 11kV | ea | 250000 | 20000 | 2021-08-01 | 141.3% | 131.5% | 379525.98 | 0 | E: 4; F: 1518103.92; Q: 2; R: 2
3.4.18 | 88kV Surge Arrester | ea | 15000 | 600 | 2021-08-01 | 141.3% | 131.5% | 21982.48 | 24 | E: 12; F: 263789.76; I: 6; R: 6
3.4.19 | 33kV Surge Arrester | ea | 8000 | 400 | 2021-08-01 | 141.3% | 131.5% | 11829.2 | 12 | E: 12; F: 141950.4; I: 6; Q: 6
3.4.20 | 11kV Surge Arrester | ea | 8000 | 400 | 2021-08-01 | 141.3% | 131.5% | 11829.2 | 12 | E: 12; F: 141950.4; Q: 6; R: 6
3.4.21 | LED Luminaire | ea | 2500 | 500 | 2021-08-01 | 141.3% | 131.5% | 4189.8 | 32 | E: 32; F: 134073.6; G: 8; K: 8; O: 8; T: 8
0
3.5 | Hardware | [7 empty] | 0
3.5.1 | Clamps - Lot | ea | 16800 | 2400 | 2021-01-01 | 168.9% | 155.9% | 32114.48 | 507 | E: 9; F: 289030.32; F: 2; G: 1; H: 2; J: 1; K: 1; L: 2
0
3.6 | Stringing | [7 empty] | 0
3.6.1 | Centipede AAC Conductor | m | 200 | 95 | 2021-01-01 | 168.9% | 155.9% | 485.88 | 324 | E: 648; F: 314850.24; G: 324; K: 324
3.6.2 | Bull AAC Conductor | m | 250 | 120 | 2021-01-01 | 168.9% | 155.9% | 609.3 | 222 | E: 444; F: 270529.2; G: 222; K: 222
3.6.6 | 120 X 4mm Aluminium Tubular Busbar 12m Lengths | ea | 5000 | 75 | 2021-01-01 | 168.9% | 155.9% | 8561.22 | 21 | E: 21; F: 179785.62; G: 21
3.6.7 | 80 X 8mm Aluminium Tubular Busbar 6m Lengths | ea | 7500 | 50 | 2021-01-01 | 168.9% | 155.9% | 12744.39 | 9 | E: 9; F: 114699.51; G: 9
0
3.7 | Control Plant | [7 empty] | 0
3.7.1 | HV Feeder Protection & Metering | ea | 980000 | 50000 | 2021-08-01 | 141.3% | 131.5% | 1450392.34 | 4 | E: 6; F: 8702354.04; F: 2; H: 4
3.7.2 | Transformer Protection & Metering | ea | 1020000 | 85000 | 2021-08-01 | 141.3% | 131.5% | 1552937.43 | 8 | E: 6; F: 9317624.58; I: 2; Q: 2; R: 2
3.7.3 | MV Breaker Protection & Metering | ea | 330000 | 25000 | 2021-08-01 | 141.3% | 131.5% | 499133.12 | 13 | E: 21; F: 10481795.52; J: 2; K: 1; L: 2; N: 2; O: 1; P: 2; S: 2; T: 1; U: 8
3.7.4 | AC/DC Panel | ea | 275000 | 12000 | 2021-08-01 | 141.3% | 131.5% | 404327.35 | 1 | E: 2; F: 808654.7; G: 50%; K: 50%; O: 50%; T: 50%
3.7.5 | Buszone | ea | 375000 | 25000 | 2021-08-01 | 141.3% | 131.5% | 562713.36 | 2 | E: 3; F: 1688140.08; G: 100%; K: 100%; O: 100%
3.7.6 | Control Cables | Lot | 250000 | 100000 | 2021-08-01 | 141.3% | 131.5% | 484735.87 | 14.1 | E: 12.4; F: 6010724.788; F: 2; H: 2; J: 2; L: 2; N: 2; P: 2; S: 20%; U: 20%
3.9.1 | Basic SCADA & Telecontrol Installation | ea | 650000 | 45000 | 2021-08-01 | 141.3% | 131.5% | 977561.69 | 1 | E: 2; F: 1955123.38; G: 50%; K: 50%; O: 50%; T: 50%
5.11.1 | Battery Charger Complete with Batteries and AC/DC Panel | ea | 425000 | 75000 | 2021-08-01 | 141.3% | 131.5% | 699114.24 | 1 | E: 4; F: 2796456.96; G: 100%; K: 100%; O: 100%; T: 100%
0
3.8 | 33kV Cable Work | [7 empty] | 0
3.8.1 | 800mm2 Al, Single Core, XLPE 33kV Cable | m | 1200 | 35 | 2021-08-01 | 141.3% | 131.5% | 1741.5 | 0 | E: 43800; F: 76277700; M: 43800
3.8.2 | Optical fibre 48-core | m | 30 | 10 | 2021-08-01 | 141.3% | 131.5% | 55.54 | 7300 | E: 405442; M: 7300
3.8.3 | Sleeves for optical fibre | m | 25 | 5 | 2021-08-01 | 141.3% | 131.5% | 41.9 | 7300 | E: 305870; M: 7300
3.8.4 | Termination: 800mm2 Al, Single Core, XLPE 33kV Cable Indoor | ea | 5000 | 2500 | 2021-08-01 | 141.3% | 131.5% | 10352.28 | 0 | E: 12; F: 124227.36; M: 12
3.8.5 | Termination: 800mm2 Al, Single Core, XLPE 33kV Cable Outdoor | ea | 7500 | 2500 | 2021-08-01 | 141.3% | 131.5% | 13884.51 | 0 | E: 0; F: 0; M: 0
3.8.6 | Joint: 800mm2 Al, Single Core, XLPE 33kV Cable | ea | 7500 | 3000 | 2021-08-01 | 141.3% | 131.5% | 14542.08 |  | E: 150; F: 2181312; M: 144
3.8.7 | Excavation: 33kV cables | m3 |  | 375 | 2021-01-01 | 168.9% | 155.9% | 375 |  | E: 5256; F: 1971000; M: 5256
0
3.9 | Commissioning | [7 empty] | 0
3.9.1 | Complete Commissioning of Substation | Sum |  | 1450000 | 2021-08-01 | 141.3% | 131.5% | 1906929.21 | 1 | E: 1; F: 1906929.21; G: 25%; K: 25%; O: 25%; T: 25%
4 | Other
4.1 | HV line costs | km | 1500000 | 1000000 | 2021-08-01 | 141.3% | 131.5% | 3434464.66 | 1 | E: 5; F: 17172323.3; E: 5
4.2 | EIA - Substation / Lines | Sum |  | 300000 | 2021-08-01 | 141.3% | 131.5% | 394537.08 | 1 | E: 1; F: 394537.08; E: 20%; G: 20%; K: 20%; O: 20%; T: 20%
4.3 | Geotechnical study - Substation / Lines | Sum |  | 300000 | 2021-08-01 | 141.3% | 131.5% | 394537.08 | 1 | E: 1; F: 394537.08; E: 20%; G: 20%; K: 20%; O: 20%; T: 20%
4.4 | Surveying - substations & Lines | Sum |  | 30000 | 2021-08-01 | 141.3% | 131.5% | 39453.71 | 1 | E: 1; F: 39453.71; E: 20%; G: 20%; K: 20%; O: 20%; T: 20%
4.5 | Professional fees - substation / lines | Sum |  | 13858802.2077 |  |  |  | 13858802.2077 | 1 | 1 | 13858802.2077 | 6.299% | 3.115% | 6.046% | 3.898% | 12.09% | 1.532% | 4.046% | 1.43% | 29.49% | 1.864% | 3.174% | 1.492% | 8.237% | 10.87% | 0.7773% | 2.883% | 2.758%
0
| Total | [7 empty] | 0 |  | 309035697.532 | 19504128.9971 | 9646993.3534 | 18722183.4696 | 12069473.9114 | 37445773.4627 | 4743541.929 | 12528069.6183 | 4428138.9771 | 91320185.5081 | 5773516.0532 | 9827999.7684 | 4621362.8373 | 25506440.8153 | 33645465.3734 | 2407029.9725 | 8928451.6344 | 8541001.3707
| Number of units | [10 empty] | 5 | 2 | 1 | 2 | 2 | 2 | 1 | 2 | 14600 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 8
| Cost per units | [10 empty] | 3900825.7994 | 4823496.6767 | 18722183.4696 | 6034736.9557 | 18722886.7313 | 2371770.9645 | 12528069.6183 | 2214069.4886 | 6254.8072 | 2886758.0266 | 9827999.7684 | 2310681.4186 | 12753220.4076 | 16822732.6867 | 1203514.9863 | 8928451.6344 | 1067625.1713
| Cost per unit rounded to nearest 10 000 for values above R1 000 000, nearest R1 000 for values between R10 000 and R100 000, and to nearest R100 for values below R10 000 | [10 empty] | 3900000 | 4820000 | 18720000 | 6030000 | 18720000 | 2370000 | 12530000 | 2210000 | 6300 | 2890000 | 9830000 | 2310000 | 12750000 | 16820000 | 1200000 | 8930000 | 1070000
| Cost excl. P&G's and Prof. Fees | [10 empty] | 17338028.874 | 8575612.34 | 16642925.0765 | 10729055.74 | 33287100.47 | 4216731.08 | 11136720.4765 | 3936356.32 | 81178298.88 | 5132317.78 | 8736516.4465 | 4108121.02 | 22673732.695 | 29908849.055 | 2139708.734 | 7936870.8165 | 7592450.214
| Pro-rata cost share excl. P&G's and Prof Fees | [10 empty] | 6.299% | 3.115% | 6.046% | 3.898% | 12.09% | 1.532% | 4.046% | 1.43% | 29.49% | 1.864% | 3.174% | 1.492% | 8.237% | 10.87% | 0.7773% | 2.883% | 2.758%

## Detail costing retic
XYZ LOCAL MUNICIPALITY
ASSET VALUE ESTIMATION METHOD
CALCULATION SHEET FOR RETICULATION NETWORK UNIT COSTS
A | B | C | [5 empty] | D | E | F | E | F | G | H | I | J | K | L | M | N | O | P
88/33/11kV/400V | [7 empty] | No of Bays / meter cable or km line |  |  | 2000 | 2 | 1 | 8 | 300 | 1 | 1 | 100 | 1 | 1 | 1 | 0.2
No. | Description | UoM | Material | Labour | Base date [YYYY/MM/01 -will display MMM-YY] | Escalation Material rate | Escalation Labour rate | Rate | Total Qty | Total amount | 2x 11kV 400mm2 Al 1x3C XLPE Type B Feeders | 11kV incomers (Switching sub) | 11kV bus-couplers and other common associated cost (Switching sub) | 11kV feeder breakers (switching sub) | 11kV feeder ring | RMU - 11kV connection | Minisub | LV feeder | LV Kiosk | 11kV o/head line | Pole transformer | LV o/head line
1 | Preliminary & General cost | Sum | [5 empty] | 1118286.074 | 100% | 1118286.074 | 18.1% | 9.682% | 27.84% | 33.89% | 1.773% | 3.341% | 4.581% | 0.5097% | 0.1105% | 0.1732% | 0% | 0%
2 | 11kV switching substation building works
2.1 | Substation Building suitable for 11kV Indoor Switchgear. | m² | 5520 | 2480 | 2021-01-01 | 168.9% | 155.9% | D: 13188.88; E: 72; F: 949599.36; G: 72
2.2 | Earthmat | m2 | 112.09 | 100.26 | 2021-01-01 | 168.9% | 155.9% | D: 345.61; E: 112; F: 38708.32; G: 112
2.4 | 25-35mm dia Yardstone 100mm thick layer | m³ | 78 | 12 | 2021-01-01 | 168.9% | 155.9% | D: 150.44; E: 280; F: 42123.2; G: 280
2.5 | Galvanised Pallissade Fence | m | 1213.83 | 476.21 | 2021-01-01 | 168.9% | 155.9% | D: 2792.41; E: 76; F: 212223.16; G: 76
3 | Substation primary plant equipment
3.1 | 11kV Indoor Incomer Breaker | ea | 300000 | 10000 | 2021-01-01 | 168.9% | 155.9% | D: 522247.66; E: 2; F: 1044495.32; F: 2
3.2 | 11kV Indoor Bus-Section Breaker | ea | 275000 | 10000 | 2021-01-01 | 168.9% | 155.9% | D: 480026.21; E: 1; F: 480026.21; G: 1
3.3 | 11kV Indoor Feeder Breaker | ea | 250000 | 10000 | 2021-01-01 | 168.9% | 155.9% | D: 437804.76; E: 8; F: 3502438.08; H: 8
4 | Substation Control Plant
4.1 | MV Breaker Protection & Metering | ea | 100000 | 10000 | 2021-08-01 | 141.3% | 131.5% | D: 154440.64; E: 11; F: 1698847.04; F: 2; G: 1; H: 8
4.2 | AC/DC Panel | ea | 50000 | 5000 | 2021-08-01 | 141.3% | 131.5% | D: 77220.32; E: 1; F: 77220.32; G: 100%
4.3 | Battery Charger Complete with Batteries and AC/DC Panel | Sum | 425000 | 75000 | 2021-08-01 | 141.3% | 131.5% | D: 699114.24; E: 1; F: 699114.24; G: 100%
4.4 | Basic SCADA & Telecontrol Installation | Sum | 250000 | 25000 | 2021-08-01 | 141.3% | 131.5% | D: 386101.6; E: 1; F: 386101.6; G: 100%
4.5 | Control Cables | Item | 100000 | 40000 | 2021-08-01 | 141.3% | 131.5% | D: 193894.35; E: 1; F: 193894.35; G: 100%
4.6 | Substation commissioning | Lot |  | 500000 | 2021-08-01 | 141.3% | 131.5% | D: 657561.8; E: 1; F: 657561.8; G: 100%
5 | 11kV Cable Work - primary cables
5.1 | 400mm2 Al, three Core, XLPE 11kV Cable | m | 495 | 35 | 2021-08-01 | 141.3% | 131.5% | D: 745.41; E: 2000; F: 1490820; E: 2000
5.2 | Optical fibre 12-core | m | 30 | 10 | 2021-08-01 | 141.3% | 131.5% | D: 55.54; E: 1000; F: 55540; E: 1000
5.3 | Sleeves for optical fibre | m | 25 | 5 | 2021-08-01 | 141.3% | 131.5% | D: 41.9; E: 1000; F: 41900; E: 1000
5.4 | Termination: 400mm2 Al, three Core, XLPE 11kV Cable Indoor | ea | 5000 | 1800 | 2021-08-01 | 141.3% | 131.5% | D: 9431.69; E: 4; F: 37726.76; E: 4
5.5 | Termination: 400mm2 Al, three Core, XLPE 11kV Cable Outdoor | ea | 5000 | 2500 | 2021-08-01 | 141.3% | 131.5% | D: 10352.28; E: 0; F: 0; E: 0
5.6 | Joint: 400mm2 Al, three Core, XLPE 33kV Cable | ea | 5000 | 2500 | 2021-08-01 | 141.3% | 131.5% | D: 10352.28; E: 6; F: 62113.68; E: 6
5.7 | Excavation: 11kV cables | m3 |  | 375 | 2021-01-01 | 168.9% | 155.9% | D: 584.63; E: 1440; F: 841867.2; E: 1440
6 | 11kV Cable Work - secondary cables
6.1 | 70mm2 Al, three Core, XLPE 11kV Cable | m | 220 | 35 | 2021-08-01 | 141.3% | 131.5% | D: 356.87; E: 315; F: 112414.05; I: 300; N: 15
6.2 | Termination: 70mm2 Al, three Core, XLPE 11kV Cable Indoor | ea | 5000 | 1800 | 2021-08-01 | 141.3% | 131.5% | D: 9431.69; E: 3; F: 28295.07; I: 1; N: 2
6.3 | Joint: 70mm2 Al, three Core, XLPE 33kV Cable | ea | 5000 | 2500 | 2021-08-01 | 141.3% | 131.5% | D: 10352.28; E: 1; F: 10352.28; I: 1
6.4 | Excavation: 11kV cables | m3 |  | 375 | 2021-01-01 | 168.9% | 155.9% | D: 584.63; E: 207; F: 121018.41; I: 207
7 | 11kV Retic equipment
7.1 | 500 kVA 11000/400V Minisub Type B | ea | 420000 | 20000 | 2021-08-01 | 141.3% | 131.5% | D: 619717.97; E: 1; F: 619717.97; K: 1
7.2 | Plinth for RMU | ea | 10000 | 5000 | 2021-08-01 | 141.3% | 131.5% | D: 20704.56; E: 1; F: 20704.56; K: 1
7.3 | Ring main unit with CT/VT unit | ea | 310000 | 10000 | 2021-08-01 | 141.3% | 131.5% | D: 451148.39; E: 1; F: 451148.39; J: 1
7.4 | Plinth for RMU | ea | 8000 | 3500 | 2021-08-01 | 141.3% | 131.5% | D: 15906.08; E: 1; F: 15906.08; J: 1
8 | LV U/G retic
8.1 | LV breaker in minisub | ea | 6000 | 500 | 2021-08-01 | 141.3% | 131.5% | D: 9134.93; E: 1; F: 9134.93; L: 1
8.2 | LV Feeder - 120mm2 Al 4-core | m | 190 | 10 | 2021-08-01 | 141.3% | 131.5% | D: 281.6; E: 100; F: 28160; L: 100
8.3 | 70mm2 BCEW | m | 130 | 5 | 2021-08-01 | 141.3% | 131.5% | D: 190.25; E: 100; F: 19025; L: 100
8.4 | Terminate LV feeder cable | ea | 1000 | 250 | 2021-08-01 | 141.3% | 131.5% | D: 1741.67; E: 2; F: 3483.34; L: 2
8.5 | Terminate BCEW | ea | 50 | 25 | 2021-08-01 | 141.3% | 131.5% | D: 103.52; E: 2; F: 207.04; L: 2
8.6 | Excavations for LV cable | m3 |  | 200 | 2021-08-01 | 141.3% | 131.5% | D: 263.02; E: 42.75; F: 11244.105; L: 42.75
8.7 | LV Kiosk- 9way | ea | 10000 | 1000 | 2021-08-01 | 141.3% | 131.5% | D: 15444.06; E: 1; F: 15444.06; M: 1
| Professional fees - substation | Sum |  | 1509686.1999 |  |  |  | 1509686.1999 | 99.83% | 1507070.8255 | 18.1% | 9.682% | 27.84% | 33.89% | 1.773% | 3.341% | 4.581% | 0.5097% | 0.1105% | 0.1732% | 0% | 0%
| Total | [8 empty] | 16603932.8245 | 3005601.5563 | 1607811.4008 | 4622523.6816 | 5628700.2816 | 294461.6954 | 554860.7104 | 760821.9656 | 84650.245 | 18347.5433 | 28769.1188 | 0 | 0
| Number of units | [9 empty] | 2000 | 2 | 1 | 8 | 300 | 1 | 1 | 100 | 1 | 1 | 1 | 0.2
| Cost per units | [9 empty] | 1502.8008 | 803905.7004 | 4622523.6816 | 703587.5352 | 981.539 | 554860.7104 | 760821.9656 | 846.5025 | 18347.5433 | 28769.1188 | 0 | 0
| Cost per unit rounded to nearest 1000 for values above R100000, nearest R100 for values between R10000 and R10000, and to nearest R10 for values below R10000 | [9 empty] | 1500 | 804000 | 4623000 | 704000 | 980 | 555000 | 761000 | 850 | 18300 | 29000 | 0 | 0
| Cost excl. P&G's and Prof. Fees | [9 empty] | 2529967.64 | 1353376.6 | 3891013.2 | 4737963.2 | 247863.38 | 467054.47 | 640422.53 | 71254.415 | 15444.06 | 24216.43 | 0 | 0
| Pro-rata cost share excl. P&G's and Prof Fees | [9 empty] | 18.1% | 9.682% | 27.84% | 33.89% | 1.773% | 3.341% | 4.581% | 0.5097% | 0.1105% | 0.1732% | 0% | 0%

## Detail costing OHL
Rates in SUPPLY RATE / INSTALL RATE are at the base date below. Escalation to the latest index is applied inside the TOTAL AMOUNT column.
DESCRIPTION |  |  | SUPPLY RATE | INSTALL RATE | TOTAL AMOUNT |  | MV | LV | TRFR
ESCALATION APPLIED base date >>> |  | 2021-01-01 | 1.6889 | 1.559 | << escalators
Pegging out the works
MV Pegging - excl bush clearing and tree felling | km | 3 | 0 | 5000 | 23385.395 |  | 1
LV Pegging - excl bush clearing and tree felling | km | 19 | 0 | 1500 | 44432.2506 |  |  | 1
Bush Clearing and Tree Felling | m | 3 | 0 | 10.5 | 49.1093 |  | 1000 | 1000
67866.7549
Digging Holes
LV stay back-actor or hand | e.a. | 1 |  | 300 | 467.7079 |  |  | 5
Compressors | e.a. | 1 |  | 1187 | 1850.5643 |  |  | 2
MV stay back-actor or hand | e.a. | 1 |  | 350 | 545.6592 |  | 3
Compressors | e.a. | 1 |  | 1396.68 | 2177.4609 |  | 1
7m Pole back-actor or hand | e.a. | 1 |  | 175 | 272.8296
Compressors | e.a. | 1 |  | 1192.67 | 1859.4039
9m Pole back-actor or hand | e.a. | 1 |  | 185 | 288.4199 |  |  | 12
Compressors | e.a. | 1 |  | 1300 | 2026.7342 |  |  | 3 | 1
10m Pole back-actor or hand | e.a. | 1 |  | 1450 | 2260.5882
Compressors | e.a. | 1 |  | 195 | 304.0101
11m Pole back-actor or hand | e.a. | 1 |  | 215 | 335.1907 |  | 9
Compressors | e.a. | 1 |  | 1400 | 2182.6369 |  | 1
12m Pole back-actor or hand | e.a. | 1 |  |  | 0 |  |  |  | 1
Compressors | e.a. | 1 |  |  | 0
14571.2058
Plant poles
7m Wood 120-140mm tops | e.a. | 1 | 695 | 45 | 1243.9125
9m Wood 140-160mm tops | e.a. | 1 | 865 | 55 | 1546.6086 |  |  | 15
9m Wood 160-180 mm tops | e.a. | 1 | 920 | 70 | 1662.8812 |  |  |  | 1
10m Wood 160-180mm tops | e.a. | 1 | 1120 | 95 | 2039.6284
10m Wood 180-200mm tops | e.a. | 1 | 1320 | 100 | 2385.1952
11m Wood 160-180mm tops | e.a. | 1 | 1400 | 140 | 2582.6649 |  | 10
11m Wood 180-200mm tops | e.a. | 1 | 1550 | 140 | 2835.9936
12m Wood 180-200mm tops | e.a. | 1 | 1850 | 140 | 3342.651 |  |  |  | 1
13m Wood 180-200mm tops | e.a. | 1 | 1986 | 140 | 3572.3356
21211.871
THREE PHASE
Int ass stag vertical ( 0 deg )3ph | e.a. | 1 | 683 | 100 | 1309.3926 |  | 7
Strain ass delta (30-60 deg) | e.a. | 1 | 2250 | 85 | 3932.4477
Strain ass delta (60-90 deg) | e.a. | 1 | 2150 | 85 | 3763.5619 |  | 2
T-off ass int vert | e.a. | 1 | 1265 | 85 | 2268.9226 |  | 1
Terminal ass vert | e.a. | 1 | 1125 | 100 | 2055.8679
In-line strain vert | e.a. | 1 | 1398 | 120 | 2548.1066
15878.2993
MV Stays
1 Off conv anchor | e.a. | 12 | 650 | 205 | 17008.2971 |  | 4
1 Off flying stay | e.a. | 9 | 1350 | 300 | 24728.9957 |  | 0.5
1 Off strut pole 9m | e.a. | 10 | 1200 | 155 | 22682.7867 |  | 0.5
64420.0794
LV Structures
Int / susp (0-30 deg) | e.a. | 1 | 350 | 35 | 645.6662 |  |  | 10.5
Strain (0-60 deg) | e.a. | 1 | 850 | 55 | 1521.2757
Strain (60-90 deg) | e.a. | 1 | 850 | 55 | 1521.2757 |  |  | 3
Terminal | e.a. | 1 | 550 | 30 | 975.6427 |  |  | 1.5
T-off from interm | e.a. | 1 | 650 | 35 | 1152.3236
T-off from strain | e.a. | 1 | 900 | 35 | 1574.5381
Cross int-int ass | e.a. | 1 | 400 | 30 | 722.314
Cross int-strain ass | e.a. | 1 | 550 | 30 | 975.6427
9088.6788
LV Stays | Unit
1 Off conv anchor | e.a. | 1 | 450 | 205 | 1079.5865 |  |  | 6
1 Off flying stay | e.a. | 1 | 1150 | 300 | 2409.8946 |  |  | 0.75
1 Off strut pole 7m | e.a. | 1 | 500 | 155 | 1086.0781 |  |  | 0.75
4575.5592
Service Boxes | Unit
1 - 2 Way box : 1 x 63 A mcb | e.a. | 1 | 859 | 10 | 1466.3193
1 - 4 Way box : 1 x 63 A mcb | e.a. | 1 | 1355 | 15 | 2311.788 |  |  | 15
3778.1072
Stringing | Unit
Fox conductor | m | 1 | 13 | 20 | 53.1357
Mink conductor | m | 1 | 20 | 20 | 64.9577
Hare conductor | m | 1 | 31 | 45 | 122.5108 |  | 3050
Squirrel conductor | m | 1 | 10 | 45 | 87.0448
Wolf conductor | m | 1 | 60 | 45 | 171.4877
35 mm sq ABC 1-ph | m | 1 | 30 | 20 | 81.8463
35 mm sq ABC 2-ph | m | 1 | 35 | 20 | 90.2906
35 mm sq ABC 3-ph | m | 1 | 50 | 15 | 107.8283 |  |  | 283.5
70 mm sq ABC 3-ph | m | 1 | 81 | 20 | 167.978 |  |  | 441
95 mm sq ABC 3-ph | m | 1 | 95 | 20 | 191.622 |  |  | 0
MV full tension joint | e.a. | 1 | 850 | 30 | 1482.3001
LV joint 35 mm full tension | e.a. | 1 | 450 | 25 | 798.9618
LV joint 70 mm full tension | e.a. | 1 | 485 | 25 | 858.0718
4278.0354
Transformer Installation
100kVA x 3 Ph (2 off) - new | e.a. | 1 | 69856 | 6500 | 128110.5347 |  |  |  | 1
50kVA x 3 Ph (0 off) - new | e.a. | 1 | 48500 | 3500 | 87366.2046
32kVA x 2 Ph (0 off) - new | e.a. | 1 | 36450 | 2500 | 65456.4395
25kVA x 3 Ph (0 off) - new | e.a. | 1 | 30025 | 2000 | 53826.0137
16kVA x 1 Ph (1 off) - new | e.a. | 1 | 25014 | 1850 | 45129.2924
379888.4849
LV Protection Morsdorf type fuses
63 A Single Phase (16kVA] | e.a. | 1 | 450 | 95 | 908.0936
80A Dual phase (32kVA) | e.a. | 1 | 800 | 120 | 1538.1696
80A Three Phase (50kVA) | e.a. | 1 | 1200 | 140 | 2244.8933 |  |  |  | 4
160A Three Phase (100kVA) | e.a. | 1 | 1600 | 175 | 2975.0024
7666.1588
Installation Earthing | Unit
MV Earthing (Type 1 crowfoot) | e.a. | 1 | 1250 | 450 | 2812.6343 |  |  |  | 1
LV Earthing (Type 1 crowfoot) | e.a. | 1 | 1000 | 450 | 2390.4198 |  |  |  | 4
Bonding | e.a. | 1 | 185 | 45 | 382.5949
5585.6491
Pole Numbering | Unit
MV pole number | e.a. | 1 | 22.5 | 10 | 53.5896 |  | 10
LV pole number | e.a. | 1 | 24.5 | 7 | 52.2902 |  |  | 15
105.8798
Commissioning | Unit
Test & commission trsf and MV equipment | e.a. | 1 |  | 5000 | 7795.1317 |  |  |  | 1
7795.1317
Other | Unit
Link assembly ( On-load) per phase | e.a. | 1 | 4500 | 650 | 8613.2281
Link assembly (Off load) per phase | e.a. | 1 | 2600 | 650 | 5404.3979
Drop-out fuses three phase | e.a. | 1 | 2850 | 450 | 5514.8071 |  |  |  | 1
Drop-out fuses dual phase | e.a. | 1 | 2200 | 350 | 4261.1468
Sample line /Material Board | sum | 1 | 12500 |  | 21110.7248
CT/VT unit, incl meter box, links | e.a. | 1 | 68520 | 8500 | 128972.2731
Remove existing poles | e.a. | 1 | 650 | 350 | 1643.4169
Remove existing conductor | m | 1 | 450 | 55 | 845.7325
Remove existing stay | e.a. | 1 | 400 | 35 | 730.1091
Remove existing transformer | e.a. | 1 | 400 | 120 | 862.6264
Remove existing dressing | e.a. | 1 | 150 | 20 | 284.5092
Ant-clim device | e.a. | 1 | 50 | 20 | 115.6234 |  |  |  | 1
Equipment Labeling | ea | 1 | 40 | 15 | 90.9397 |  |  |  | 1
178449.5351
House Connections | Unit
'Supply ECU base, fixing rails and plug | ea | 1 | 95 | 25 | 199.4172 |  |  | 60
Overhead connection | ea | 1 | 150 | 35 | 307.8946 |  |  | 60
Customer Interface Unit | ea | 1 | 158 | 25 | 305.8152 |  |  | 60
Supply 60A ED (no internal ELPU) | ea | 1 | 395 | 65 | 768.4356 |  |  | 60
Sealing of meters | ea | 1 | 15 | 5 | 33.128 |  |  | 60
COC certificates | ea | 1 | 1500 | 500 | 3312.8001 |  |  | 60
Supply and install additional 63A circuit breaker | ea | 1 |  | 95 | 148.1075
Supply and install additional 63A circuit breaker | ea | 1 |  | 95 | 148.1075
Capture and upload of customer data new & Existing | e.a. | 1 |  | 60 | 93.5416 |  |  | 60
5317.2474
Excavate and plant poles
5m Wood 80-100 mm tops | e.a.
Compressors | e.a.
7m Wood 120-140 mm tops | e.a. | 1 | 750 | 95 | 1414.751
Compressors | e.a. | 1 | 1350 | 75 | 2396.8853
Shackpole Dressing | e.a. | 1 | 310 | 35 | 578.1119
Compressors | e.a.
4389.7481
Conductor (Installation incl service conn. rate)
4mm sq Airdac | m | 1 | 26.5 | 15 | 68.1401
10mm sq Airdac (with communication core) | m | 1 | 45.65 | 20 | 108.2769 |  |  | 1200
[5 empty] | 176.417 | per Trfr Zone | 592229.8219 | 725530.9197 | 170013.1898
[5 empty] | 24796.2322 | per conn. | 9870.497 | 12092.182 | 2833.5532
[6 empty] | unit | km | km | ea
[6 empty] | per unit | 582521.1363 | 1001422.9396 | 170013.1898
Note on C3: Zibusiso Ndlovu: Base date for every rate on this sheet. Matches the Jan-2021 base date used on 'Detail costing substation works' and 'Detail costing retic'. Change here to re-date the whole sheet.
Note on D3: Zibusiso Ndlovu: Material escalator = WG 162 (Electrical reticulation) latest index / index at base date. Applied to the SUPPLY RATE column.
Note on E3: Zibusiso Ndlovu: Labour escalator = WG 160 (Electrical installations) latest index / index at base date. Applied to the INSTALL RATE column.
Note on A159: Author: Should we remove
Note on A160: Author: Should we remove
Note on A161: Author: Should we remove
Note on A162: Author: Should we remove